Hot Tub Control update 20130326

@ Hot Tub:

Measure:
Water Temperature
Heat Temperature
Air Temperature

Inputs:
Pool Controller
Low speed – 220V / Optocoupler
High speed -220V / Optocoupler
Thermostat – dry contacts
Heat Demand – 220V / Optocoupler

Outputs:
Pump
Low speed – 220V
High speed – 220V
Digikey PB308-ND – SPDT – Use 3 of them – 12V / 83ma Coil $4/ea

Control circuit:
3 Power Relays (High-speed, Low-speed, Common) driven by 3 SSR's on PCB.

Data Flow:
Xmit –
Demand
Pool Temperature
Air Temperature
Rec – Circulate for heat

Current Grainger relays
1YDA1 – 24VAC-50ma; 10A contact DPDT
6CWX8 – 24VAC-168ma; 30A contact DPDT - $14.91 – Magnecraft 92S11A22D-24A
Allied Electronics 70185035, $8.52/ea – only 3 amps on NC Contact
Allied 70132397 - $2.75/ea – 30A SPST-NO ; 24VAC 100 ohm American Zetler -	AZ2280-1A-24A

Controller Summary:
3	Relay outputs: high-speed, low-speed, common, Heat Demand
2	Thermister in: Water temp, Air Temp
3	HiVoltage in: High-speed, Low-speed, Heat Demand
1	Thermostat in: ??
1	Long-term timer
1	Watchdog timer

Logic:
Initialize (or watch dog reset): All Relays off
TubOccupied = Last High-Speed Request + 20 minutes
High-Speed Request => Pump High-Speed
(Low-Speed Request & ! Heat Demand) || \
(Heat Demand & (Heat >Tub)) || \
(Low-Speed Request & TubOccupied) => Pump Low Speed

@ Pool
Measure:
Pool temperature - Thermistor
Relative humidity – Silicon Labs Si7005-GM1R – I2C interface
Sense (7)
Garage Demand - Techmar
Storage Demand - Honeywell
Connector Demand – Techmar
Modine Demand - Honeywell
Pool Floor Demand - Techmar
Pool heat Demand – Techmar
Hot Tub Demand
Control (8)
Pool filter circulator – Add a relay
Hot Tub circulator - Taco
Garage circulator - Taco
Storage circulator - Taco
Connector circulator - Taco
Pool Floor Circulator – Taco
Pool Heat Circulator
Modine Circulator
Data Flow

@ Bunker

Starter Board:
Inputs:
DHW Demand – 24VAC – Aquastat is a dry contact – a transformer has been added to drive the Tekmar 260 controller – we go back to the dry contact
Outputs:
DHW Circulator – 120VAC Relay NO Dry Contact
Furnace DHW Request – 24VAC – use existing transformer with our relay output

Measure:
Boiler Temperature
DHW Temperature
Exterior Temperature
Sense:
Floor Demand
Basement Demand
Stair Demand
DHW Demand
HighTempDemands = modineDemand || immediateTubDemand || (Time && (poolDemand || tubDemand)
Additional:
New Box 1st Floor Air
New Box 3rd Floor Air
Basement
Basement Stairs
Old Box 1st Floor
Old Box 2nd Floor
Offices
1st Floor Heat

Control

DHW circulator = DHW Demand (our own circuit)
Boiler Set point(DHW input) = DHW Demand || HiTempDemands
GarageLoop/Boiler Demand = (time &&(garageDemand || storageDemand || connectorDemand || poolFloorDemand)) || HiTempDemands

Generalized solution

Digital inputs
6 x Dry Contact inputs
3 x High Voltage Inputs – opto couplers – Newark 36J9622 Avago HCPL-817-300E $0.15/ea
Forward current transfer ratio is > 50%. 10K Load; 3.3V Supply => 0.3 ma output =>
1 ma input; @240V => 220K input resistor; time constant = 0.05 sec =>
c = .05/2.2e5 = .22 uf; throw in 1 uf for good measure

Analog Inputs
3 x Temperature inputs
1 x Relative humidity input

Digital outputs
6 x 60VAC; 350ma solid state relay outputs – Newark AQY282S Panasonic AQY282S operating current = 1.8 ma; $1.70/ea – Allied 70158430 $1.40

Thermistor measurements:

1/T = 1/T0 + 1/β ln (R/R0)

R∞ = R0 e (- β/T0)

T = β/ln(R/R∞)

ln(R) = β/T + ln(R∞)

T is in ºK

β = 3977

T0 = 25 ºC = 298.15 ºK

R0 = 10,000 Ω

Rb = 10,000 Ω

R = Rb(1024/n *(3.3/2.56) - 1)

R∞ = 1.61e-2

A/D readings are scaled on 2.56V but source to thermistors is 3.3V, so the output must be scaled
System Logic

Tub Data:
Tub Occupied
Tub Heat Request

Pool Data:
Modine Heat Request

Bunker Data:
High Temp Heat Available